### GUIDELINE MASTER

### ACOUSTICAL LOUVER SPECIFICATIONS

[INSERT THIS SECTION IN PART 2 – PRODUCTS OF THE APPROPRIATE SECTION WITHIN DIVISION 15, MECHANICAL SYSTEMS]

2.XX	ACOUSTICAL LOUVERS

[Use the one of the following two paragraphs.]

2.XX.1	Louver frame shall be constructed with 16 gauge (1.63 mm) minimum [galvanized steel // stainless steel].  Louver blades shall be [flat // herringbone // airfoil] configuration and made of 18 gauge (1.24 mm) minimum solid [galvanized steel // stainless steel], and 22 gauge (0.81 mm) minimum perforated [galvanized steel // stainless steel].

2.XX.1	Louver frame shall be constructed with 14 gauge (1.63 mm) minimum aluminum.  Louver blades shall be [flat // herringbone // airfoil] configuration and made of 16 gauge (1.29 mm) minimum solid aluminum, and 20 gauge (0.81 mm) minimum perforated aluminum or expanded metal.

[Use the one of the following two paragraphs.]

2.XX.2	Acoustical fill shall MoldBlock MediaTM insulation containing natural cotton fibers treated with a borate solution to actively inhibit the growth of mold, bacteria and fungi.  Media shall not contain any formaldehydes or VOC’s.  Media shall be 100% recyclable.  Media shall comply with UL181 and NFPA 90A.  Glass fiber, fiberglass and rockwool will not be permitted as substitutes for MoldBlock MediaTM insulation.

2.XX.2	Acoustical fill shall be bacteria and fungus resistant, shot-free glass fiber insulation.  Glass fiber density and compression shall be as required to insure conformance with laboratory test data.

2.XX.3	Acoustical media shall be encapsulated with [fiberglass cloth // non-woven fabric // Tedlar] [as indicated on the drawings] to minimize erosion and impregnation of the glass fiber.  [The fabric shall be fire retardant, complying with NFPA 90A and shall also be treated with a fungal inhibitor and water repellant finish.]

[Anodized finish is for aluminum louvers only.  Other finishes are available.]

2.XX.4	Louvers shall be [supplied with a standard mill finish // supplied with a prime coat for field painting onsite by others // finished with a satin coat / galvaneal material for painting onsite by others // supplied with a baked enamel finish; color as directed by the Architect // anodized; clear or color as directed by the Architect].

2.XX.5	Louver acoustical and aerodynamic performance shall be as indicated on the schedule.

2.XX.5	Louver acoustical performance shall be determined per ASTM E90-02.  Louver aerodynamic performance shall be determined per AMCA Standard 500-L-99.  Manufacturer shall submit certified data substantiating both the specified acoustic and aerodynamic performance.

2.XX.6	Acceptable manufacturers: Vibro-Acoustics (basis of design).