# SPECIFICATION

Section 15xxx – Vibro-Acoustics Acoustic Barrier Walls

# Part 1 – General

  - Related Documents

- General: Comply with the general Conditions and all applicable Contract Documents.

  - Work Included:  Each Enclosure and Plenum shall be a complete assembly with                        sealant, assembly hardware (bolts, screws etc.), access doors.

  - Submittals

- Product Data:  Submit manufacturer’s technical product data for enclosure or plenum showing dimensional, weights, capacities, ratings, finishes of materials, and installation instructions.

- Shop Drawings:  Submit shop drawings showing unit dimensions, weight loading, Required clearances, field connection details and methods of support. Draw to a scale of 3/8” to one foot, using same sheet size as Contract Drawings. Including dampers and duct connections

- Quality Assurance

##### Manufacturer’s Responsibility:  Enclosure or plenum manufacturer shall have sole source responsibility for the design, factory fabrication and supply of all components and equipment as noted below.  Provide enclosure/plenums that are a product of an equipment manufacturer regularly engaged in the production of such product. Unit components and equipment fabricated and supplied by the contractor will not be permitted.

- Contractor’s Responsibility: The Contractor shall be responsible for the field assembly of the enclosure/plenum per the instructions and submittal documents supplied by the manufacturer.  The Contractor shall provide the manufacturer with all field dimensions, mounting locations and duct openings as required to coordinate the design and fabrication of the enclosure or plenum.

- Codes and Standards:  Provide enclosures and plenums conforming to the following:

- National Fire Protection Association (NFPA): Provide enclosure/plenum internal insulation complying with NFPA 90A, “Standard for the Installation of Air Condition and Ventilating Systems”.

- Sheet Metal and Air Conditioning Contractors’ National Association, Inc. (SMACNA): Comply with applicable SMACNA standards including “HVAC Duct Construction Standards - Metal and Flexible”.

- Delivery, Storage and Handling

- Delivery:  Deliver components on factory shipping skids  Pack small components in factory-fabricated protective containers.

- Handling: Handle components carefully to avoid damage to components, enclosures, and finishes.  Do not install damaged components; replace and return damaged components to product manufacturer.

- Storage:  Store components in a clean dry place and protect from weather and construction traffic.

- Unloading:  Comply with manufacturer’s rigging and installation instructions for unloading and moving them to final location

Part 2-Product:

2.1 	Manufacturers

- Acceptable manufacturers: Vibro-Acoustics

- Enclosures or Plenums

- Physical dimensions must be maintained as shown on the contract drawings. If dimensions are different from that shown, the owner and engineer must be advised at the time of bid review.

- Design enclosure/plenum to be suitable for the maximum, total wind loading under design conditions.

### Construction

- Barrier Panels: Panels shall be 4” tongue and groove type.  The exterior sheet shall be a minimum of 18 gauge (1.18 mm) G90 galvanized steel.  The interior sheet shall be a minimum of 22 gauge (0.78 mm) G90 galvanized perforated steel. Panels shall be filled  with fiberglass acoustic media.

- Removable Panels: Where indicated on the plans, bolted panels of the Internal Flange Butt Connection type shall be provided for equipment removal.  Panels shall be 4” with construction as noted above.

- Structural Support Steel:  Structural steel shall be provided by the enclosure or plenum manufacturer so the maximum deflection of the assembled panels is L/180.  Structural  to structural steel connections shall be fully welded.

- Media:  Media shall be incombustible, acoustical quality, shot-free fiberglass insulation with long, resilient fibers bonded with a thermosetting resin.  Fiberglass shall be packed with 15% compression during panel assembly.  Media shall be bacteria and fungus resistant and conform to irregular surfaces.  Media shall not cause or accelerate corrosion of aluminum or steel.  Mineral wool will not be permitted as a substitute for fiberglass.

- Access Doors: Doors shall be provided as noted on the plans.  Doors shall be 4” x 24” wide x 72” high with the same construction as the acoustic panels, except that the interior sheet shall be solid.  Doors shall be mounted in a 10 ga. galvanized steel angle frame with a single “P” gasket.  Hardware shall include 2 cam-type Ventlok 310 latches and 2 butt hinges.  Where indicated, doors shall be supplied with 12” x 12” inspection windows, double-glazed with wire reinforced glass mounted in a neoprene U-gasket.

- Performance:  The acoustical performance of the panels shall be equal to or greater than the following:

### Octave Band Hz		63	125	250	500	1K	2K	4K	8K

###### Transmission Loss		18	 21	  27	 37	48	 54	 54	54

###### Absorption Coefficients	 -	 0.7	  0.9	0.99   0.99	 0.9	 0.8	  -

The panel design shall have  maximum combustion ratings as noted below  when tested in accordance with ASTM E84, NFPA 255 or UL 723.

Panel materials including glass fiber:

Flamespread Classification:	15

Smoke Development Rating:	  5

# Text boxes

## S5

## ENCLOSURE