Unit Cleaning Specification

Manufacturing Precautions and Cleaning Instructions for Silencers & Acoustic Panels used in Clean Room and Pharmaceutical Applications

General Notes:

- The steel used on the subject project shall not have the manufacturers label or 	     stamping on any surface.

- No writing (i.e. tagging with grease pencils or other types of marker) shall be permitted on any surface of the steel.

- Project tagging shall be permitted, where approved by the customer, on the external surface of completed silencers.

Silencer Cleaning:

The cleaning of silencers for the subject project is a two part process.

- All surfaces of the steel used for the fabrication of silencers shall be cleaned after primary machining (shear, brake, roll forming) and prior to final assembly.

- All exposed steel surfaces of assembled silencers shall receive a final wipe down and vacuum prior to wrapping and sealing for shipment.

Procedure:

- Solid casing material shall be cleaned with a mixture of 50/50 isopropyl alcohol and distilled water.

- Perforated materials shall be cleaned using either a mixture of 50/50 isopropyl alcohol and distilled water or 100 % isopropyl alcohol as needed to remove all traces of oil, petroleum based materials and particulate contamination.

Primary cleaning prior to assembly:

- Use a mixture of isopropyl alcohol as stated above and wipe on steel surfaces with a very wet wipe (use waterproof gloves).

- Move the steel to a clean wash down area and rinse with clean tap water through a power washer.

- After letting the material air dry, place the steel on a clean poly sheet or skid and cover with clean poly

Final cleaning:

- After final assembly , wipe all surfaces with a mixture of 50/50 isopropyl alcohol with a damp not soaking wet wipe

- Remove residual particles with a HEPA filtered vacuum cleaner

- Visually inspect all surfaces for cleanliness

Packaging:

Upon completion of the cleaning and inspection processes, the ends of each silencer shall be shrink-wrapped for shipment.